## PV_HP_self
External PHPP file
|  |  | path: | C:\1_data\bigshare\projects\000_older_projects\Passive Houses\PHPP_9\06_Master_CD_PHPP_V9.6a_EN_20160709\01_PHPP | [7 empty] | IMPORTANT: PHPP must be opened!
|  |  | filename: | PHPP_V9.6a_EN_Example.xlsx
|  |  | Language: | 2-English
Information for the current version
It works only for monovalent systems i.e. "No flow type heater", "No direct electricity (except of pumps)"
A solar thermal system can be included
Only one HP can be included
This sheet is tested with PHPP version 9.6b (German) and version 9.6a (English)
This vesion includes the electricity of the appliances and auxiliaries from only a residential building
internal notes
GHX pump is included in the monthly distribution, even though it is a simplification
information about the filename and path: capital or small letters do not play a role
Inputs from external file | [18 empty] | 2
[5 empty] | Wel_H | Wel_DHW | Wel_tot |  | SPF | Wel_H | Wel_DHW | Wel_HP | [6 empty] | Version 9.1 | Version 9.6a
[5 empty] | kWh | kWh | kWh |  |  | kWh | kWh | kWh | [6 empty] | 1-German | 2-English
sheet: | HP |  |  | cell: | $V$150 | $W$150 | $M$139 |  | $M$132 | $V$149 | $W$149 | $M$128 | [6 empty] | WP | HP
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
sheet: | Climate | theta_src | theta amb | °C | E$24 | F$24 | G$24 | H$24 | I$24 | J$24 | K$24 | L$24 | M$24 | N$24 | O$24 | P$24 |  |  | Klima | Climate
sheet: | HP |  | theta gw | °C | BD249 | BD250 | BD251 | BD252 | BD253 | BD254 | BD255 | BD256 | BD257 | BD258 | BD259 | BD260 |  |  | WP | HP
sheet: | HP |  | theta vghx/hghx | °C | BD308 | BD309 | BD310 | BD311 | BD312 | BD313 | BD314 | BD315 | BD316 | BD317 | BD318 | BD319 |  |  | WP | HP
sheet: | HP |  | HP source |  | BD249 BD308: $M$166 |  |  | WP | HP
sheet: | HP |  | theta snk_H | °C | BD249 BD308: $M$23 |  |  | WP | HP
sheet: | HP |  | control |  | BD249 BD308: M182 |  |  | WP | HP
sheet: | HP |  | theta i_set |  | BD249 BD308: M150 |  |  | WP | HP
sheet: | HP |  | theta snk_DHW | °C | BD249 BD308: $M$37 |  |  | WP | HP
sheet: | SolarDHW |  | HD | kWh | F$97 | G$97 | H$97 | I$97 | J$97 | K$97 | L$97 | M$97 | N$97 | O$97 | P$97 | Q$97 |  |  | SolarWW | SolarDHW
sheet: | SolarDHW |  | DHW + losses | kWh | F$123 | G$123 | H$123 | I$123 | J$123 | K$123 | L$123 | M$123 | N$123 | O$123 | P$123 | Q$123 |  |  | SolarWW | SolarDHW
sheet: | SolarDHW |  | HD covered by ST | kWh | F$130 | G$130 | H$130 | I$130 | J$130 | K$130 | L$130 | M$130 | N$130 | O$130 | P$130 | Q$130 |  |  | SolarWW | SolarDHW
sheet: | SolarDHW |  | DHW covered by ST | kWh | F$129 | G$129 | H$129 | I$129 | J$129 | K$129 | L$129 | M$129 | N$129 | O$129 | P$129 | Q$129 |  |  | SolarWW | SolarDHW
sheet: | PV |  | PV | kWh | N63 | N64 | N65 | N66 | N67 | N68 | N69 | N70 | N71 | N72 | N73 | N74 |  |  | PV | PV
sheet: | Electricity |  | Electiricty appliances | kWh | N63: AA35 |  |  | Strom | Electricity
sheet: | Aux Electricity |  | Aux. electricty | kWh | N63: V42 |  |  | Hilfsstrom | Aux Electricity
sheet: | Verification |  | Treated floor area | m2 | N63: I34 |  |  | Nachweis | Verification
Read cells from external file
[5 empty] | Wel_H | Wel_DHW | Wel_tot |  | SPF | Wel_H | Wel_DHW | Wel_HP
[5 empty] | kWh | kWh | kWh |  |  | kWh | kWh | kWh
[5 empty] | 1000.7707 | 651.2332 | 1652.0039 |  | 1.6284 | 1000.7707 | 651.2332 | 1652.0039
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  |  | theta amb | °C | 0.4 | 1.3 | 4.4 | 8.4 | 12.9 | 16.3 | 17.6 | 17 | 13.9 | 9.4 | 4.7 | 1.6
|  |  | theta gw | °C | 1.6957 | 3.8431 | 7.5408 | 12.0006 | 15.9198 | 18.2436 | 18.3466 | 16.1498 | 12.3135 | 7.8524 | 3.967 | 1.7029
|  |  | theta vghx/hghx | °C | 10.4235 | 10.4193 | 10.419 | 10.4226 | 10.4291 | 10.4369 | 10.4439 | 10.448 | 10.4484 | 10.4448 | 10.4382 | 10.4304
HP source | bar: 1
|  |  | theta snk_H | °C | 1: 55
control | bar: 1
|  |  | theta i_set |  | 1: 20
|  |  | theta snk_DHW | °C | 1: 60
|  |  | HD | kWh | 631.809 | 271.1416 | 97.0603 | 0.023398 | 5.0883e-07 | 7.4213e-12 | 8.0541e-13 | 5.7529e-14 | 7.7889e-08 | 0.87542 | 347.1128 | 628.4026
|  |  | DHW + losses | kWh | 319.202 | 288.3115 | 319.202 | 308.9052 | 319.202 | 308.9052 | 319.202 | 319.202 | 308.9052 | 319.202 | 308.9052 | 319.202
|  |  | HD covered by ST | kWh | 0 | 83.9452 | 81.5216 | 0.023398 | 5.0883e-07 | 7.4213e-12 | 8.0541e-13 | 5.7529e-14 | 7.7889e-08 | 0.87542 | 15.362 | 0
|  |  | DHW covered by ST | kWh | 0 | 7.9086 | 60.7193 | 212.7897 | 248.7293 | 236.5296 | 249.1496 | 247.9044 | 197.8496 | 115.6285 | 0 | 0
|  |  | PV | kWh | 271.3621 | 536.7903 | 742.2229 | 1095.8866 | 1277.0844 | 1188.2391 | 1233.7927 | 1205.9652 | 955.9336 | 630.9476 | 301.1111 | 195.5903
|  |  | Electiricty appliances | kWh | 1: 1727.169
|  |  | Aux. electricty | kWh | 1: 481.7325
|  |  | Treated floor area | m2 | 1: 156
Check if PHPP is open: | bar: 1 to 12
Monthly temepratures
theta snk H |  |  | Qmon_min | kWh | 1: 0; 2: theta_i; 3: °C; 4: 20; 5: a; 6: 0.055396
|  |  | Qmon_max | kWh | 1: 631.809; 2: tehta_snk_H_design; 3: °C; 4: 55; 5: b; 6: 20
|  |  | theta src | °C | 0.4 | 1.3 | 4.4 | 8.4 | 12.9 | 16.3 | 17.6 | 17 | 13.9 | 9.4 | 4.7 | 1.6
|  |  | theta snk_H | °C | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  |  | theta snk_DHW | °C | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Optional user inputs |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
User inputs: |  |  | theta src | °C
User inputs: |  |  | theta snk_H | °C
User inputs: |  |  | theta snk_DHW | °C
Calculations inputs
|  |  | Treated floor area | m2 | 1: 156
[5 empty] | Wel_H | Wel_DHW | Wel_tot |  | SPF | Wel_H | Wel_DHW | Wel_HP
[5 empty] | kWh | kWh | kWh |  |  | kWh | kWh | kWh
[5 empty] | 1000.7707 | 651.2332 | 1652.0039 |  | 1.6284 | 1000.7707 | 651.2332 | 1652.0039
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | a
|  |  | theta src | °C | 0.4 | 1.3 | 4.4 | 8.4 | 12.9 | 16.3 | 17.6 | 17 | 13.9 | 9.4 | 4.7 | 1.6
|  |  | theta snk_H | °C | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  |  | theta snk_DHW | °C | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Q_HP_HD | kWh | 631.809 | 187.1964 | 15.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.7508 | 628.4026 | 1794.6975
|  |  | Q_HP_DHW | kWh | 319.202 | 280.4029 | 258.4827 | 96.1155 | 70.4728 | 72.3756 | 70.0524 | 71.2976 | 111.0556 | 203.5735 | 308.9052 | 319.202 | 2181.1379
|  |  | days per month |  | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | 365
Results
n_carnot_H | 0.29104 |  | 1/COP_carnot_H |  | 0.16639 | 0.16364 | 0.1542 | 0.14201 | 0.12829 | 0.11793 | 0.11397 | 0.1158 | 0.12525 | 0.13896 | 0.15328 | 0.16273
n_carnot_DHW | 0.54609 |  | 1/COP_carnot_DHW |  | 0.1789 | 0.1762 | 0.16689 | 0.15489 | 0.14138 | 0.13117 | 0.12727 | 0.12907 | 0.13838 | 0.15188 | 0.16599 | 0.1753
|  |  | COP_H |  | 1.7492 | 1.7785 | 1.8875 | 2.0495 | 2.2685 | 2.4678 | 2.5536 | 2.5133 | 2.3237 | 2.0944 | 1.8987 | 1.7885
|  |  | COP_DHW |  | 3.0525 | 3.0993 | 3.2721 | 3.5257 | 3.8626 | 4.1631 | 4.2908 | 4.2309 | 3.9464 | 3.5954 | 3.2898 | 3.1152 |  |  | SPF calc | SPF PHPP
|  |  | Wel_H | kWh | 361.2015 | 105.255 | 8.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.7234 | 351.3583 | 1000.7707 | 0 | 1.7933 | 1.7933
|  |  | Wel_DHW | kWh | 104.5711 | 90.4733 | 78.9962 | 27.2611 | 18.2449 | 17.385 | 16.3263 | 16.8517 | 28.1411 | 56.6202 | 93.8967 | 102.4656 | 651.2332 | 0 | 3.3492 | 3.3492
|  |  | Wel_HP | kWh | 465.7726 | 195.7283 | 87.2288 | 27.2611 | 18.2449 | 17.385 | 16.3263 | 16.8517 | 28.1411 | 56.6202 | 268.62 | 453.8239 | 1652.0039 | 0 | 2.4067 | 2.4067
|  |  | Electiricty appliances | kWh | 146.6911 | 132.4952 | 146.6911 | 141.9591 | 146.6911 | 141.9591 | 146.6911 | 146.6911 | 141.9591 | 146.6911 | 141.9591 | 146.6911 | 1727.169
|  |  | Aux. electricty | kWh | 40.9143 | 36.9548 | 40.9143 | 39.5945 | 40.9143 | 39.5945 | 40.9143 | 40.9143 | 39.5945 | 40.9143 | 39.5945 | 40.9143 | 481.7325
|  |  | Wel_tot | kWh | 653.3779 | 365.1783 | 274.8341 | 208.8146 | 205.8503 | 198.9385 | 203.9317 | 204.457 | 209.6947 | 244.2256 | 450.1736 | 641.4293 | 3860.9054
|  |  | PV | kWh | 271.3621 | 536.7903 | 742.2229 | 1095.8866 | 1277.0844 | 1188.2391 | 1233.7927 | 1205.9652 | 955.9336 | 630.9476 | 301.1111 | 195.5903 | 9634.9257 |  |  |  | Net Zero
|  |  | Absolute difference | kWh | 382.0158 | -171.612 | -467.3888 | -887.0719 | -1071.2341 | -989.3006 | -1029.861 | -1001.5081 | -746.2389 | -386.722 | 149.0625 | 445.839 | -5774.0203
|  |  | Relative difference | % | 140.8% | -31.97% | -62.97% | -80.95% | -83.88% | -83.26% | -83.47% | -83.05% | -78.06% | -61.29% | 49.5% | 227.9% | -59.93%
PV FO |  | 0.45 | PV own | kWh | 131.4794 | 116.9655 | 119.9707 | 93.9666 | 92.6326 | 89.5223 | 91.7693 | 92.0057 | 94.3626 | 109.9015 | 123.9526 | 130.5319 | 1287.0606
|  |  | W_el GRID | kWh | 521.8985 | 248.2128 | 154.8634 | 114.848 | 113.2176 | 109.4162 | 112.1624 | 112.4514 | 115.3321 | 134.3241 | 326.221 | 510.8973 | 2573.8448
|  |  | max PV own | kWh | 271.3621 | 365.1783 | 274.8341 | 208.8146 | 205.8503 | 198.9385 | 203.9317 | 204.457 | 209.6947 | 244.2256 | 301.1111 | 195.5903 | 2883.9881
|  |  | min_w_el_grid | kWh | 382.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149.0625 | 445.839 | 976.9173
|  |  | Supply Cover Factor and Load Cover Factor | [17 empty] | max
|  | SCF | Supply Cover Factor |  | 48.45% | 21.79% | 16.16% | 8.574% | 7.253% | 7.534% | 7.438% | 7.629% | 9.871% | 17.42% | 41.17% | 66.74% | 13.36% |  |  |  | 29.93%
|  | LCF | Load Cover Factor |  | 20.12% | 32.03% | 43.65% | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 27.53% | 20.35% | 33.34% |  |  |  | 74.7%
Monthly Primary Energy Evaluation
|  | fPE, non-RE | conversion factor |  | 2.01 | 1.96 | 1.89 | 1.6 | 1.33 | 1.2 | 1.18 | 1.28 | 1.53 | 1.78 | 1.92 | 2.01
|  | nonRE PE | primary energy | kWh/(m2TA·a) | 1049.016 | 486.4972 | 292.6918 | 183.7569 | 150.5795 | 131.2994 | 132.3517 | 143.9377 | 176.458 | 239.0968 | 626.3443 | 1026.9036 | 4638.9329
|  |  | Treated floor area | m2 | 1: 156
Results
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | a
|  |  | theta source | °C | 0.4 | 1.3 | 4.4 | 8.4 | 12.9 | 16.3 | 17.6 | 17 | 13.9 | 9.4 | 4.7 | 1.6
|  |  | theta sink SH | °C | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  |  | theta sink DHW | °C | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | q_HP SH | kWh/(m2TA·a) | 4.0501 | 1.2 | 0.099607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1266 | 4.0282 | 11.5045
|  |  | q_HP DHW | kWh/(m2TA·a) | 2.0462 | 1.7975 | 1.6569 | 0.61612 | 0.45175 | 0.46395 | 0.44905 | 0.45704 | 0.71189 | 1.305 | 1.9802 | 2.0462 | 13.9817
|  |  | COP SH |  | 1.7492 | 1.7785 | 1.8875 | 2.0495 | 2.2685 | 2.4678 | 2.5536 | 2.5133 | 2.3237 | 2.0944 | 1.8987 | 1.7885
|  |  | COP DHW |  | 3.0525 | 3.0993 | 3.2721 | 3.5257 | 3.8626 | 4.1631 | 4.2908 | 4.2309 | 3.9464 | 3.5954 | 3.2898 | 3.1152
|  | HP SH | w_el Space Heating | kWh/(m2TA·a) | 2.3154 | 0.67471 | 0.052773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 2.2523 | 6.4152
|  | HP DHW | w_el DHW | kWh/(m2TA·a) | 0.67033 | 0.57996 | 0.50639 | 0.17475 | 0.11695 | 0.11144 | 0.10466 | 0.10802 | 0.18039 | 0.36295 | 0.6019 | 0.65683 | 4.1746
|  | HP | w_el Heat pump | kWh/(m2TA·a) | 2.9857 | 1.2547 | 0.55916 | 0.17475 | 0.11695 | 0.11144 | 0.10466 | 0.10802 | 0.18039 | 0.36295 | 1.7219 | 2.9091 | 10.5898
|  | App | w_el Appliances | kWh/(m2TA·a) | 0.94033 | 0.84933 | 0.94033 | 0.90999 | 0.94033 | 0.90999 | 0.94033 | 0.94033 | 0.90999 | 0.94033 | 0.90999 | 0.94033 | 11.0716
|  | Aux | w_el Auxiliaries | kWh/(m2TA·a) | 0.26227 | 0.23689 | 0.26227 | 0.25381 | 0.26227 | 0.25381 | 0.26227 | 0.26227 | 0.25381 | 0.26227 | 0.25381 | 0.26227 | 3.088 |  |  |  |  | min | max
|  | Tot | w_el Total | kWh/(m2TA·a) | 4.1883 | 2.3409 | 1.7618 | 1.3386 | 1.3196 | 1.2752 | 1.3073 | 1.3106 | 1.3442 | 1.5655 | 2.8857 | 4.1117 | 24.7494 |  |  |  | Net Zero | 0 | 3.9981
|  | PV | PV Yield | kWh/(m2TA·a) | 1.7395 | 3.441 | 4.7578 | 7.0249 | 8.1864 | 7.6169 | 7.9089 | 7.7305 | 6.1278 | 4.0445 | 1.9302 | 1.2538 | 61.7623 | 0 | 0 | 0 |  | 0 | 8.1864
|  |  | Absolute difference | kWh/(m2TA·a) | 2.4488 | -1.1001 | -2.9961 | -5.6864 | -6.8669 | -6.3417 | -6.6017 | -6.4199 | -4.7836 | -2.479 | 0.95553 | 2.8579 | -37.013
|  |  | Relative difference |  | 140.8% | -31.97% | -62.97% | -80.95% | -83.88% | -83.26% | -83.47% | -83.05% | -78.06% | -61.29% | 49.5% | 227.9% | -59.93%
|  | Factor of PV self consumpation: |  | 0.45
|  | PV self | PV self-consumption | kWh/(m2TA·a) | 0.84282 | 0.74978 | 0.76904 | 0.60235 | 0.5938 | 0.57386 | 0.58826 | 0.58978 | 0.60489 | 0.7045 | 0.79457 | 0.83674 | 8.2504
|  | GRID | w_el from grid | kWh/(m2TA·a) | 3.3455 | 1.5911 | 0.99271 | 0.73621 | 0.72575 | 0.70139 | 0.71899 | 0.72084 | 0.73931 | 0.86105 | 2.0912 | 3.275 | 16.499
|  |  | max PV self cons. | kWh/(m2TA·a) | 1.7395 | 2.3409 | 1.7618 | 1.3386 | 1.3196 | 1.2752 | 1.3073 | 1.3106 | 1.3442 | 1.5655 | 1.9302 | 1.2538 | 18.4871
|  |  | min_w_el from grid | kWh/(m2TA·a) | 2.4488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95553 | 2.8579 | 6.2623
|  |  | Supply Cover Factor and Load Cover Factor | [17 empty] | max
|  | SCF | Supply Cover Factor |  | 48.45% | 21.79% | 16.16% | 8.574% | 7.253% | 7.534% | 7.438% | 7.629% | 9.871% | 17.42% | 41.17% | 66.74% | 13.36% | 0 | 0 | 0 | 29.93%
|  | LCF | Load Cover Factor |  | 20.12% | 32.03% | 43.65% | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 27.53% | 20.35% | 33.34% | 0 | 0 | 0 | 74.7%
Monthly Primary Energy Evaluation
|  | fPE, non-RE | conversion factor |  | 2.01 | 1.96 | 1.89 | 1.6 | 1.33 | 1.2 | 1.18 | 1.28 | 1.53 | 1.78 | 1.92 | 2.01
|  | nonRE PE | primary energy | kWh/(m2TA·a) | 6.7245 | 3.1186 | 1.8762 | 1.1779 | 0.96525 | 0.84166 | 0.84841 | 0.92268 | 1.1311 | 1.5327 | 4.015 | 6.5827 | 29.7367
Note on H18: Author: with the well pump
Note on K20: Author: without the dir el and the elec of the pump
Note on L20: Author: without the dir el and the elec of the pump
Note on F25: 1: Air-source hp 2: GW hp 3: Vghx hp 4: Hghx hp
Note on F27: on/off:1 ideal:2
Note on H40: Author: with the well pump
Note on K42: Author: without the dir el and the elec of the pump
Note on L42: Author: without the dir el and the elec of the pump
Note on H76: Author: with the well pump
Note on K78: Author: without the dir el and the elec of the pump
Note on L78: Author: without the dir el and the elec of the pump
Note on C101: Typically 0.4 without battery, and between 0.45 and 0.55 with battery
Note on E132: Typically 0.4 without battery, and between 0.45 and 0.55 with battery
Note on D141: See also: Ochs F, Dermentzis G. Evaluation of Efficiency and Renewable Energy Measures Considering the Future Energy Mix. 7th International Building Physics Conference Proceedings, IBPC, Syracuse, New York: International Association of Building Physics (IABP); 2018, p. 1271–6. https://doi.org/10.14305/ibpc.2018.pe-1.03.